# Westville Belgium Sanitary District

Board Meeting Minutes
Date: Thursday, October 16th, 2025
Time: 6:00 PM
Location: 120 E. Main St., Westville, IL 61883

### 1. Call to Order

The meeting was called to order at 6:00 PM.

### 2. Roll Call

- Royce – Absent

- Bruce – Present

- Tom – Present

Special Guests Present:

- Larry Johnson, Engineer

- Frank Gabehart, Superintendent

- Deanna Simmonds, Office Manager

- Butch, ERH

### 3. Public Comment

No public comment.

### 4. Approval of Minutes – September 18th, 2025 Meeting

Motion made by Bruce to approve the minutes.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 5. Consideration of the Agenda – October 16th, 2025 Meeting

Motion made by Bruce to approve the agenda.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 6. Treasurer’s Report

Motion made by Bruce to approve the Treasurer’s Financial Report, including monthly expenditures and summaries.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 7. ERH Report

Motion made by Bruce to approve the ERH Report.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 8. Superintendent Report

Motion made by Bruce to approve the Superintendent Report.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 9. Office Manager Report

Motion made by Bruce to approve the Office Manager Report.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

### 10. New Business

#### a. Electrical Box Repairs at Plant

Approved to have RC Electrical complete repairs on the electrical boxes at the plant.
Total cost: $6,138.30 (materials and labor).
Motion made by Bruce.
Roll Call: Bruce – Yes, Tom – Yes
Motion Passed.

#### b. Jules Street Investigation – Village of Westville

A call was received from Mike Bennett regarding a sewer odor near the park, coming from storm runoff north of the park.
Findings:

- Jules Street Lift Station was backed up due to a pump being kicked out and failing to switch to the backup pump.

- Sean (ERH) responded and took water samples; EPA in Champaign was notified.

- Pump was found clogged, cleaned, and returned to working order.

- OmniSite was contacted regarding alarm acknowledgment; once district acknowledges an alarm, OmniSite indicates it becomes the district’s responsibility.

- pH and ammonia levels from the lift station discharge tested low.

- Sean will follow up with OmniSite regarding possible alarm adjustments.

#### c. Signing of Ordinance 25-1 – Budget 2025–2026

Signed by Bruce and Deanna during the meeting.
Royce signed on Friday, October 17th.
Frank delivered the ordinance to the courthouse for filing.

#### d. Signing of Ordinance 325-2 – Tax Levy 2025–2026

Signed by Bruce and Deanna during the meeting.
Royce signed on Friday, October 17th.
Frank delivered the ordinance to the courthouse for filing.

### 11. Follow-Up from Superintendent and ERH

Smoke testing, dye testing, and camera inspection were performed around the Jules Street Lift Station area.
No definitive source of inflow or odor found.
The Village of Tilton assisted by bringing down their camera truck for additional inspection.

### 12. Unfinished Business

#### EPA Loan & USDA-RD Loan Updates

Larry Johnson provided updates:

- An amendment must be filed for the EPA loan to update project items, specifically to include cleaning and recoating the stainless steel digester lid.

- Estimated cost: $500,000 to lift, clean, and recoat the lid, which has not been serviced in approximately 40 years.

- Fehr Graham Engineering will prepare the required amendment.

- Motion to add the cleaning and coating of the digester lid and to add to the EPA and  USDA loan was approved by Bruce and Tom.

USDA-RD Loan:

- No update at this time due to the federal government shutdown.

- An amendment will also be required for the USDA loan.

### 13. Special Announcements

None.

### 14. Adjournment

Meeting adjourned at 6:28 PM